## Directions
Water Use Efficiency Compliance Documentation – Directions
Compliance Forms
Compliance forms are provided in the User’s Manual to assist in understanding and documenting compliance with each section's requirements.
To demonstrate compliance with the Standard’s requirements for this section, projects must demonstrate compliance with mandatory measures.
Header Information
Project Name: Enter the name of the project. This should agree with the name that is used on the plans and specifications or the common name used to refer to the project.
Project Address: Enter the street address of the project, for instance “949 Main Street, Irvine, CA 92618.”
Date: Enter the date when the compliance documentation was completed.
Designer of Record/Telephone: Enter the name and the telephone number of the designer of record.
Contact Person/Telephone: Enter the name and telephone number of the person who should be contacted if there are questions about the compliance documentation.
City: The city where the project is located.
Instructions
For each item in the compliance forms, there is the option to indicate that 1) the project complies with the requirement or 2) the requirement is not applicable to the project. Select the appropriate check box.
If a requirement's exception(s) apply to the project, check the appropriate box.
For every item checked "complies," the documentation author should fill in the Document Reference field by citing the plans (drawing number), specifications (specifications section number), or attached calculations that document the requirement.
The documentation author should fill in the Calculated Performance Metric field on the Performance Option form with the results of applicable performance metric calculations.

## Mandatory
Water Use Efficiency Compliance Documentation – Mandatory
Project Name
Project Address: |  |  | Date:
Designer of Record: |  |  | Telephone:
Contact Person: |  |  | Telephone:
City:
Mandatory Provisions
Complies | Not applicable | Requirement | Document Reference
§6.3.1: Site Water Use Reductions
q | q | §6.3.1.1: Minimum of 60% of the area of the improved landscape shall be in bio-diverse planting of native plants and rainfall-ETc compatible plants.
q Exception: Athletic fields, golf courses and driving ranges shall be excluded from this requirement for schools, residential common areas, or public recreational facilities.
q | q | §6.3.1.2: Golf courses and driving ranges use only municipally-reclaimed water and/or alternate on-site sources of water; in other landscaped areas, a maximum of one third of improved landscape area is irrigated with potable water – all other irrigation is provided from alternate on-site sources or municipally reclaimed water.
q Exception: Potable water has been temporarily used on newly installed landscape during the landscape establishment period.
q Exception: The amount of potable water used during the landscape establishment period does not exceed 70% ETo for turfgrass and 55% ETo for other plantings.
q Exception: Municipally reclaimed water is available at a water main within 200 ft (60 m) of the project site and has been used in lieu of potable water during the landscape establishment period.
q | q | §6.3.1.2.1: The irrigation system is designed by an accredited or certified irrigation professional and following the requirements of section 6.3.1.2.1.
q | q | §6.3.1.2.1: Automatic irrigation systems have been hydrozoned to water different plant materials.
q | q | §6.3.1.2.1: Sprinklers are not spraying water directly on a building and are not located within 3 ft (0.92 m) of any building.
q | q | §6.3.1.2.2: Irrigation system is controlled by a qualifying smart controller.
q | q | §6.3.1.2.2: Smart controller uses evapotranspiration and weather data or on-site rain sensors or moisture sensors to adjust irrigation schedules.
q | q | §6.3.1.2.2: Qualifying smart controllers meet the following minimum requirements: irrigation adequacy – 80 % min ETo; irrigation excess – not to exceed 10%.
q Exception: Temporary irrigation systems used for plant establishment are exempt from this requirement.
q | q | §6.3.1.2.3: In-ground irrigation systems for rainfall-ETc compatible plants do not use potable or reclaimed water, unless plants are deemed equivalent to rainfall-ETc compatible plants per section 6.3.1.1.
§6.3.2: Building Water Use Reductions
q | q | §6.3.2.1a: Water closets (flushometer) have a max flush rate of 1.28 gal (4.8 L) per flush.
q | q | §6.3.2.1b: Water closets (tank-type) have a max flush rate of 1.28 gal (4.8 L) per flush.
q | q | §6.3.2.1c: Urinals have a max flush rate of 0.5 gal (1.9 L) per flush.
q | q | §6.3.2.1d: Public lavatory faucets have a max flow rate of 0.5 gpm (1.9 L/min).
q | q | §6.3.2.1e: Public metering faucets have a max flow rate of 0.25 gal (1.0 L) per cycle.
q | q | §6.3.2.1f: Residential lavatory faucets have a max flow rate of 1.5 gpm (5.7 L/min).
q | q | §6.3.2.1g: Residential kitchen faucets have a max flow rate of 2.2 gpm (8.3 L/min).
q | q | §6.3.2.1h: Residential showerheads have a max flow rate of 2.0 gpm (7.6 L/min).
q | q | §6.3.2.1i: Residential shower compartments have a total max flow rate of 2.0 gpm (7.6 L/min).
q Exception: If the shower compartment exceeds 2,600 in2 (1.7 m2), an additional flow of 2.0 gpm (7.6 L/min) is permitted.
q | q | §6.3.2.1j: Water-bottle filling stations are included in at least half of all drinking fountains installed indoors.
q | q | §6.3.2.2a: Dwelling unit clothes washers comply with the ENERGY STAR Program Requirements and have a max water factor of 5.4 gal/ft3 or 0.72 L/L of drum capacity.
q | q | §6.3.2.2a: Dwelling unit dishwashers comply with the ENERGY STAR Program Requirements and have a max water factor of 3.8 gal or 14.3 L/full operating cycle.
q | q | §6.3.2.2b: Publicly accessible clothes washer have a max water factor of 4.0 gal/ft3 or 0.53 L/L of drum capacity.
q | q | §6.3.2.2c: Commercial dishwashers in commercial food service facilities meet all ENERGY STAR requirements.
q | q | §6.3.2.3a: Potable water has not been used for once-through cooling in HVAC systems.
q | q | §6.3.2.3b: For cooling tower makeup water having < 200 ppm (200 mg/L) of total hardness (expressed as calcium carbonate), at least 5 cycles of concentration have been achieved.
q | q | §6.3.2.3b: For cooling tower makeup water having > 200 ppm (200 mg/L) of total hardness (expressed as calcium carbonate), at least 3.5 cycles of concentration have been achieved.
q Exception: Where the total dissolved solids concentration of the discharge water exceeds 1500 mg (1500 ppm/L), or silica exceeds 150 ppm (150 mg/L), measured as silicon dioxide, before the above cycles of concentration are reached.
q | q | §6.3.2.3c: Cooling towers have makeup and blowdown meters, conductivity controllers, and overflow alarms.
q | q | §6.3.2.3c: Cooling towers have efficient drift eliminators.
q | q | §6.3.2.3c: Drift reductions amount to a max of 0.002% of the recirculated water volume for counterflow towers and 0.005% of the recirculated water flow for cross-flow towers.
q | q | §6.3.2.3d: Condensate from AC units with a capacity > 65,000 Btu/h is recovered for reuse.
q | q | §6.3.2.4a: Potable water has not been used for roof spray systems to thermally condition the roof.
q | q | §6.3.2.4b: In-ground irrigation systems are not used for vegetated roof systems that use potable or off-site treated reclaimed water.
q | q | §6.3.2.4c: Potable water might have been used during the plant establishment period, but it has not been used to permanently irrigate the vegetated landscape.
q | q | §6.3.2.5a: Commercial food service operations use high-efficiency pre-spray valves per §6.3.2.5.
q | q | §6.3.2.5b: Commercial food service operations use dishwashers that are ENERGY STAR certified.
q | q | §6.3.2.5c: Commercial food service operations use boilerless/connectionless food steamers that consume no more than 2.0 gal/h (7.5 L/h).
q | q | §6.3.2.5d: Commercial food service operations use combination ovens that consume no more than 10 gal/h (38 L/h).
q | q | §6.3.2.5e: Commercial food service operations use air-cooled ice machines that are ENERGY STAR certified.
q | q | §6.3.2.5f: Commercial food service operations are equipped with hands-free faucet controllers within the food preparation area of the kitchen and dish room, including pot sinks and washing sinks.
q | q | §6.3.2.6a: Medical and lab facilities use only water-efficient steam sterilizers.
q | q | §6.3.2.6a: Steam sterilizers use water-tempering devices that only allow water to flow when the discharge of condensate or hot water from the sterilizer > 140oF.
q | q | §6.3.2.6a: Vacuum sterilizers use mechanical vacuum equipment in place of Venturi-type vacuum systems.
q | q | §6.3.2.6b: Medical and lab facilities use film processor water recycling units where large frame X-ray films of more than 6 inches are processed. Small dental X-ray equipment is exempt from this requirement.
q | q | §6.3.2.6c: Where the digital networks are installed, medical and lab facilities use digital imaging and radiography systems.
q | q | §6.3.2.6d: Medical and lab facilities use a dry-hood scrubber system. For projects that determine wet scrubber systems are necessary, the scrubber is equipped with a water recirculation system.
q | q | §6.3.2.6d: For medical and lab facilities that include hood washdown systems, the hood is equipped with self-closing valves
q | q | §6.3.2.6e: Medical and lab facilities use only dry vacuum pumps, unless fire and safety codes require a liquid ring pump.
q | q | §6.3.2.6f(1): For filtration processes in medical and lab facilities, pressure gauges are used to determine and display when to backwash or change cartridges.
q | q | §6.3.2.6f(2): For ion exchange and softening processes in medical and lab facilities, recharge cycles have been set by volume of water treated or based upon conductivity or hardness.
q | q | §6.3.2.6f(3): For reverse osmosis and nanofiltration equipment in medical and lab facilities with a capacity > 100 L/hour, reject water does not exceed 60% of the feed water and is used as scrubber feed water or for other beneficial uses on the project site.
q | q | §6.3.2.6f(4): For medical and lab facilities, simple distillation has not been used as a means of water purification.
q | q | §6.3.2.6g: Food service operations that are located within medical or lab facilities comply with §6.3.2.5.
§6.3.3: Special Water Features
q | q | §6.3.3a: Ornamental fountains are supplied either by alternate on-site sources of water or municipally reclaimed water.
q | q | §6.3.3a: Fountains are equipped with makeup water meters.
q | q | §6.3.3a: Fountains are equipped with leak detection devices that shut off water flow if a leak of more than 1 gallon per hour is detected.
q | q | §6.3.3a: Fountains are able to recirculate, filter, and treat all water for reuse within the system.
q Exception: For fountains where alternate on-site sources of water or municipally reclaimed water are not available with 500 ft (150 m) of the building project site, potable water is allowed to be used for water features with less than 10,000 gal (38,000 L) capacity.
q | q | §6.3.3b(1): Pools and spas must recover filter backwash water for reuse on landscaping or other applications, or treat and reuse backwash water within the system.
q | q | §6.3.3b(2): For pools and spas that use removable cartridges, only reusable cartridges and systems are used.
q | q | §6.3.3b(2): For pools and spas that contain filters with backwash capabilities, only pool filter equipment has been used that includes a pressure drop gauge to determine when the filter needs to be backwashed and a sight glass enabling the operator to determine when to stop the backwash cycle.
q | q | §6.3.3b(3): If pool and spa splash troughs are provided, they drain back into the pool or spa.
§6.3.4: Water Consumption Measurement
q | q | §6.3.4.1: Measurement devices with remote communication capability have been provided to collect the water consumption data for each water supply source (e.g., potable, reclaimed, rainwater) to the building that exceeds the thresholds listed in Table 6.3.3A.
q | q | §6.3.4.1: Both potable and reclaimed water entering the building are being monitored or sub-metered.
q | q | §6.3.4.1: Sub-meters have been provided for individual leased, rented, or other tenant or sub-tenant space with any building totaling > 50,000 ft2 (5000 m2).
q | q | §6.3.4.1: Sub-meters have been provided for any project, building, tenant, or sub-tenant space within a project or building where water consumption > 1,000 gal/day (3800 L/day) or per Table 6.3.4.1.A.
q | q | §6.3.4.1: Sub-metering with remote communication capabilities has been provided to collect water use data for each of the subsystems listed in Table 6.3.4.1.B.
q | q | §6.3.4.2: Measurement devices installed on systems using more than 1,000 gal/day (3800 L/day) of water are configured to communicate water consumption data to a meter data management system. At a minimum meters provide daily data and record hourly consumption of water.
q | q | §6.3.4.3: The meter data management system is capable of electronically storing water meter, monitoring systems, and sub-meter data.
q | q | §6.3.4.3: The meter data management system creates user reports showing calculated hourly, daily, monthly, and annual water consumption for each measurement device and sub-meter.
q | q | §6.3.4.3: The meter data management system provides alarm notification capabilities to support the requirements of §10.3.2.1.2.
§6.3.5: Water Softeners
q | q | §6.3.5.1: Water softeners are equipped with demand-initiated regeneration control systems (no timer-base systems).
q | q | §6.3.5.2: Water softeners shall have a maximum water consumption during regeneration of more more than 4 gal per 1000 grains of hardness removed (15.1 L per 17.1 g/L).
q | q | §6.3.5.3: Waste water from water softener regeneration does not discharge to reclaimed water collection systems and follows the IPC.
q | q | §6.3.5.4: Water softeners installed meet the efficiency and listing requirements of section 6.3.5.4.
§6.3.6: Reverse Osmosis Water Treatment Systems
q | q | §6.3.6.1: Reverse osmosis systems are equipped with an automatic shutoff valve.
q | q | §6.3.6.1: Point-of-use reverse osmosis treatment system for drinking water are listed and labeled to NSF 58.
§6.3.7: On-Site Reclaimed Water Treatment
q | q | §6.3.7: On-site reclaimed water treatment systems are listed and labeled in accordance with NSF 350.
§6.3.8: Dual Water Plumbing Supply
q | q | §6.3.8.1: The building water supply system has been constructed to allow the supply of reclaimed or alternative water to all urinals and water closets.
q Exception: the building scope of work does not include water supply systems for urinals or water closets, or the toilets or urinals are designed to operate without the use of water.
q Exception: sufficient supply of reclaimed water or alternate on-site sources of water are not available or expected to be available per section 6.3.8.1.
Signature: Date:
Printed Name: License/Registration #:
Company Name: