CHAPTER 1

APPLICATION AND ADMINISTRATION

SECTION 101
GENERAL

101.1 Purpose. The purpose of this standard is to establish the minimum physical and fire performance properties and requirements for spray-applied polyurethane foam plastic thermal insulation to demonstrate compliance with the intent of the model building codes for a variety of construction applications. This standard also establishes basic installation requirements.

SECTION 102
SCOPE

102.1 Scope. This standard applies to single- and multiple-component spray-applied polyurethane foam plastic insulation and sealants intended for use in a variety of nonstructural building construction applications. This standard is limited to spray-applied foam plastic insulation that is sprayed in place where, during the application, the spray-applied foam plastic insulation is applied in a liquid or frothed state and permitted to free-rise and cure in situ.

This standard provides diversified test procedures for qualifying fire performance characteristics of spray-applied foam plastic insulation exceeding the maximum thickness tested in accordance with ASTM E84 or UL 723 and for qualifying alternative ignition barrier assemblies and alternative thermal barrier assemblies.

SECTION 103
COMPLIANCE ALTERNATIVES

103.1 Compliance alternatives. Nothing in this standard is intended to prevent the use of designs, products or technologies as alternatives to those prescribed by this standard, where equivalence is provided, and such equivalence is approved by the administrative authority adopting this standard.

SECTION 104
REFERENCED DOCUMENTS

104.1 Referenced documents. The codes and standards referenced in this standard shall be considered part of the requirements of this standard to the prescribed extent of each such reference. Chapter 4 contains a complete list of all referenced standards.

Use of the most recent edition of a standard referenced in Chapter 4 is assumed unless the standard year is referenced in the applicable building code. Appendix A contains additional information correlating standard year editions referenced within the 2006 through 2024 code editions. The body of this standard references sections of the 2024 Edition of the International Codes. Appendix B contains additional information correlating code section references to code editions.

CHAPTER 2

DEFINITIONS

SECTION 201
GENERAL

201.1 General. For the purpose of this standard, the terms listed in Section 202 have the indicated meaning.

201.2 Undefined terms. The meaning of terms not specifically defined in this document or in referenced standards shall have ordinarily accepted meanings such as the context implies.

201.3 Interchangeability. Words, terms and phrases used in the singular include the plural and the plural the singular.

SECTION 202
DEFINED TERMS

AIR IMPERMEABLE INSULATION. An insulation which, at a given thickness, allows a maximum total air leakage rate of 0.02 L/s-m2 (0.004 ft3/min-ft2) when tested at a 75 Pa pressure differential in accordance with ASTM E283 or ASTM E2178, as amended in this standard.

ALL CONSTRUCTION PLANES. Within an attic or crawl space, any surface exposed to the interior space of the attic or crawl space regardless of its orientation within that space.

ALTERNATIVE IGNITION BARRIER ASSEMBLY. An assembly consisting of either the exposed spray-applied foam plastic or the spray-applied foam plastic with a fire-protective covering, that has been tested in accordance with and complies with the conditions of acceptance of Section 302.4 through 302.6 of this standard.

ALTERNATIVE THERMAL BARRIER ASSEMBLY. An assembly consisting of either the exposed spray-applied foam plastic or the spray-applied foam plastic with a fire-protective covering, that has been tested in accordance with and complies with Section 2603.9  Special Approval of the International Building Code or Section R303.6Specific Approval of the International Residential Code and meets the conditions of acceptance of Section 302.4 of this standard.

CLOSED CELL FOAM. Spray applied foam plastic with a Closed Cell content of 90% or greater.

COVERING. A material forming a protective layer or membrane, including boards, sheet goods or liquid-applied coating materials, installed to protect spray-applied foam plastic from exposure to fire or environmental conditions such as  moisture or ultra-violet light.

FREE RISE. A condition of application wherein the spray-applied foam plastic is applied to a substrate or within a cavity and allowed to expand in at least one direction without constraint.

IGNITION BARRIER. A fire-protective covering applied or installed over spray-applied foam plastic insulation in attics and crawlspaces to increase the time it takes for the foam plastic to become involved in a fire.

INSULATION APPLICATIONS. Insulation applications are those applications where the spray-applied foam plastic insulation is applied on or in building elements or construction assemblies which are not roofing applications.

ROOFING APPLICATIONS. Roofing applications are those applications wherein the spray-applied foam plastic insulation is applied to the exterior of a roof deck as a component of a roof covering or roof assembly.

SEALANT FOAMS: Single component spray applied polyurethane foam plastic applied in beads less than one inch thick.

SPRAY-APPLIED FOAM PLASTIC. Single- and multi-component, spray-applied polyurethane foam plastic insulation used in nonstructural applications which are installed at locations wherein the material is applied in a liquid or frothed state, permitted to free rise and cure in situ.

THERMAL BARRIER. A fire-protective covering which separates the spray-applied foam plastic insulation from the interior of the building and is designed to slow the temperature rise of the foam during a fire situation and delay its involvement in the fire.

UTILITIES. For the purposes of attic and crawlspace entry, utilities include, but are not limited to, mechanical equipment, electrical wiring, fans, plumbing, fuel-fired or electric hot water heaters, and fuel-fired or electric furnaces.

CHAPTER 3

PHYSICAL AND PERFORMANCE REQUIREMENTS

SECTION 301
PHYSICAL PROPERTIES

301.1 General. Spray-applied plastic foam insulation shall comply with the requirements as stated in Table 1,2, 3 or 4 as applicable. Where the number of test specimens is not specified in the applicable test methods,no fewer than five specimens shall be used. The required testing is described in the following sections:

3.01.1.1 	Basic Fire Properties.  Spray foam for wall, attic, basement, crawlspace and floor applications shall meet the basic requirements in Section 302.2.

3.01.1.2 Thermal Barrier and Ignition Barrier: Spray-applied foam plastic insulation shall be separated from the building interior by a thermal barrier conforming to IBC Section 2603.4 or IRC Section 302.4. Alternatively, specific assemblies shall be approved based on testing laid out in Sections 302.3-6

3.01.1.3 Types I-IV Construction: Spray-applied foam plastic insulation used in Types I-IV Construction shall be approved based on testing laid out in Section 302,7

3.01.1.4 Roofing. Spray-applied foam plastic insulation used in roofing applications shall comply with the requirements in Section 302.8.

3.01.1.5 Sealants. Spray-applied foam plastic sealants shall comply with the requirements in Section 302.9.

301.2 Thermal resistance. Thermal resistance shall be determined in accordance with ASTM C177, ASTM C518 or ASTM C1363. Test specimen density shall be within ±10 percent of the nominal density intended for use.

The reporting of thermal resistance shall be based on a mean-test temperature of 75°F ± 5°F (23.8°C ± 2.8°C) with a temperature gradient not less than 40°F (22°C). At the option of the manufacturer, supplemental thermal resistance values at other mean temperatures shall be included. R-values of less than 10 shall be rounded to the nearest tenth. R-values of 10 or more shall be rounded to the nearest whole number.

The thermal-resistance (R-values) for the spray-applied foam plastic shall be established for the range of thicknesses and the density intended for use. Nominal thicknesses tested shall be 1 inch (25.4 mm) and a thickness greater than or equal to 31/2 inches (89 mm). Calculated R-values for thicknesses between 1 inch (25.4 mm) and the maximum thickness tested shall be based on linear interpolation. Calculated R-values for thicknesses greater than the maximum thickness tested shall be extrapolated based on tested R-values at the maximum thickness tested.

Exception: For spray-applied foam plastic that is used at a thickness less than 31/2 inches, tests shall be conducted at a 1-inch (25.4 mm) thickness and at the maximum thickness intended for use. Calculated R-values shall follow the rounding and interpolation rules stated above.

All samples shall be conditioned as prepared (i.e., with skins or substrates attached) and as set forth in Table 1 or Table 2, as applicable. Samples shall be sprayed to dimensions sufficient to accommodate the test equipment and the required thickness. Samples shall be aged in the as-sprayed configuration, then cut to the required dimensions at the conclusion of the aging period.

301.3 Air permeance. Where determination of the air permeance of the spray-applied foam plastic is required, the air permeance shall be measured in accordance with ASTM E283 or ASTM E2178 to establish that the insulation qualifies as air impermeable insulation.

Testing in accordance with ASTM E283 shall be modified as follows:

1.	The test frame shall be not less than 24 inches (610 mm) square, and a 1/2-inch-thick (12.7 mm), low-density fiberboard substrate complying with ASTM C208 fastened and sealed on the panel edges. The fiberboard shall have an air permeance not less than 1.0 L/s-m2 (0.20 ft3/min-ft2).

2.	The spray-applied foam plastic insulation shall be applied at the minimum thickness that recognition is required.

3.	The test pressure difference shall be 75 Pa (1.57 lb./ft2).

4.	Air flow shall be determined in both infiltration and exfiltration conditions.

Total air leakage shall be reported as the larger result from the infiltration and exfiltration tests. When testing results confirm the air permeance equal to or less than the total air leakage rate to qualify as air impermeable insulation, the report shall state the spray foam does qualify as an air impermeable insulation at the tested thickness (report in inches).

301.4 Vapor retarder. Where determination of the vapor retarder classification of the spray-applied foam plastic is required, the vapor retarder classification shall be determined based on testing in accordance with ASTM E96, Procedure A (desiccant method). Based on the results of testing, the vapor retarder classification shall be assigned based on the following at the thickness and density tested:

- Class I: 0.1 perm or less

- Class II: > 0.1 to £ 1.0 perm

- Class III: >1.0 to £ 10 perm

SECTION 302
FIRE PERFORMANCE

302.1 General. Testing performed in accordance with the tests listed in Section 302 shall be performed on spray-applied foam plastic insulation at the maximum thickness and density intended for use. Sections 302.2 through 302.6apply to low-density and medium-density spray-applied foam plastic insulation; Section 7 applies to use in Types I-IV Construction; Section 302.8 applies to roofing applications and Section 302,9 applies Spray-applied foam plastic sealants.

302.2 Surface-burning characteristics tests.

302.2.1 Flame-spread index. The insulation shall exhibit a flame-spread index not greater than 75 when tested in accordance with ASTM E84 or UL 723 at the maximum thickness and density intended for use, but no greater than 4 inches (102 mm).

302.2.2 Smoke-developed index. The insulation shall exhibit a smoke-developed index not greater than 450 when tested in accordance with ASTM E84 or UL 723 at the maximum thickness and density intended for use, but no greater than 4 inches (102 mm).

302.2.3 Qualification of thicknesses greater than 4 inches. For spray-applied foam plastic insulation that is intended to be applied at a thickness greater than 4 inches (102 mm), the insulation shall comply with Section 302.2.1 and Section 302.2.2, and the end-use qualified based on testing in accordance with NFPA 286 (using acceptance criteria of Section 803.1.1 of the International Building Code or Section 303.6 of the International Residential Code), FM 4880, UL 1040 or UL 1715.

Exception: Under the International Residential Code, spray-applied foam plastic insulation greater than 4 inches (102 mm) shall be used under the following conditions:

- The spray-applied foam plastic insulation has a flame-spread index not greater than 25 and smoke-developed index not greater than 450 when tested in accordance with ASTM E84 or UL 723 at a thickness of 4 inches (102 mm) and the maximum density intended for use.

- The spray-applied foam plastic insulation is separated from the interior of the building by 1/2-inch (12.7 mm) gypsum wallboard or by a material that is tested in accordance with and meets the acceptance criteria of both the Temperature Transmission Fire Test and the Integrity Fire Test of NFPA 275.

302.3 Alternative thermal barrier assembly—room corner fire tests. Where the spray-applied foam plastic insulation is installed without the use of a Code-prescribed thermal barrier separating the insulation from the interior of a building, the requirements of this section shall apply.

Assemblies containing spray-applied foam plastic insulation shall be qualified by use of one of the room corner fire tests specified in Section 302.4.1, 302.4.2 or 302.4.3. The testing shall be performed on spray-applied foam plastic insulation at the maximum thickness and density intended for use. Placement of the gas burner or wood crib under this section shall comply with the maximum average measured distance between the burner or crib as shown in Figure 1.

302.3.1 NFPA 286. Where the spray-applied foam plastic insulation is tested in accordance with NFPA 286, it shall comply with the following Conditions 1 through 5:

1.	During the 40-kW exposure, flames shall not spread to the ceiling.

2.	The flame shall not spread to the outer extremity of the sample on any wall or ceiling.

3.	Flashover, as defined in NFPA 286, shall not occur.

4.	The peak heat release rate throughout the test shall not exceed 800 kW.

5.	The total smoke released throughout the test shall not exceed 1,000 m2.

302.3.2 UL 1715. Where the spray-applied foam plastic insulation is tested in accordance with UL 1715, the requirements of Sections 302.4.2.1 and 302.4.2.2 shall apply.

302.32.1 Smoke determination. Determination of excessive smoke levels shall be as follows and shall consider the following:

| 1. Visual documentation | Smoke determination shall be recorded in accordance with the visual records procedures within UL 1715; digital video and photographic documentation is permitted. Video and still photographs shall be in color and time stamped. Where a high level of smoke is generated during the test, the assembly containing spray-applied foam plastic insulation will be considered to fail the test. |
| --- | --- |
| 2. Test specimen. | For each test, when the test is for wall systems only, a new section of uncoated and unpainted 5/8-inch-thick (15.9 mm) gypsum wallboard, 2 feet by 2 feet (610 mm by 610 mm), shall be installed |

302.3.2.2 Reports of test results. The test report shall provide the details described below.

| 1. Description | Description of the room test setup, with details of the test room construction and materials tested |  |
| --- | --- | --- |
| 2. Observations | The test observations, commencing with crib ignition and ending with a final description of panels after all combustion ceases |  |
| 3. Thermocouple readings | Temperature readings from all thermocouples |  |
| 4. Concluding Statement | A statement of passing or failing based upon the conditions of acceptance. |  |
| 5. Photographic records | A photographic record of the test |  |

302.3.3 Alternative thermal barrier assembly. Where the spray-applied foam plastic insulation is installed as a component of an alternative thermal barrier assembly, the assembly shall be qualified by one or more of the following methods:

1.	Room corner fire tests in Section 302.4.1 or 302.4.2.

2.	Section 2603.9 of the International Building Code or Section R302.6 of the International Residential Code, as applicable.

Where a covering is used to cover the spray-applied foam plastic insulation, the thickness of the covering shall be identified in units appropriate for the specific covering  In the case of liquid-applied coatings, the installed thickness (in mils), in both wet film thickness and dry film thickness, and the corresponding application rate (in square feet per gallon) shall be identified and included in the test report.

Assemblies tested in accordance with Section 302.4.1 or 302.4.2 shall be limited to the construction plane for which it was tested, i.e., if the assembly was only tested with insulation in walls, it is limited to installation in walls only. Assemblies tested simultaneously with insulation in walls and ceilings shall comply as an installation on all construction planes at the same time.

Where the spray-applied foam plastic assembly is tested in accordance with NFPA 286 or UL 1715, the assembly shall be suitable for use in all ceiling heights.

302.3.3.1 FM 4880 or UL 1040. Where the spray-applied foam plastic assembly is tested in accordance with FM 4880 or UL 1040, the assembly shall be limited to use in areas with a clear ceiling height not less than 20 feet (6096 mm).

302.4 Testing for alternative ignition barrier assembly for use in attics—General. Where the spray-applied foam plastic insulation is installed as a component of an alternative ignition barrier assembly (i.e.: without the use of a code-prescribed ignition barrier separating the insulation from the interior of the attic or crawl space), the assembly shall be qualified by one of the following methods:

1.	Room corner fire tests as described in this section.

2.	Special Approval section of the International Building Code or the Specific Approval section of the International Residential Code, as applicable.

Testing shall be conducted with the foam plastic installed at the maximum density and maximum thickness intended for use.

Where the spray-applied foam plastic insulation is to be installed as a component of an alternative ignition barrier assembly (i.e., without a code-prescribed ignition barrier), the assembly shall be qualified by testing as set forth in either Section 302.4.1 (Test Method A) or 302.4.2 (Test Method B) of this standard or in the Special Approval section of the International Building Code or the Specific Approval section of the International Residential Code. Assemblies tested in accordance with Section 302.4.1 or 302.4.2 are suitable for installation on all construction planes. The requirements of this section apply to both an exposed spray-applied foam plastic insulation or to a spray-applied foam plastic insulation system using a covering.

302.4.1 Test Method A. Where Test Method A is used, testing shall be conducted in accordance with NFPA 286 with the modifications specified in this section and shall use one of the configurations specified in this section.

302.4.1.1 Coatings. Where a coating is applied over the foam, the coating thickness shall be measured using the dry-film thickness technique (DFT), using one of the methods described in either Method 1 or Method 2, as applicable.

Method 1 (Slit-sample method). Where Method 1 is used, two slit samples shall be taken within 24 inches (610 mm) of the corner where the burner will be placed. The slit samples shall be approximately 1/2-inch deep (12.7 mm), between 2 to 3 inches long (51 to 76 mm), and 1/2-inch (12.7 mm) wide. One face of the slit sample (where the measurements will be made) shall be cut perpendicular to the surface of the spray polyurethane foam.

The coating thickness shall be measured at four random locations on the face of each slit sample using an optical comparator so that eight coating thickness measurements shall be reported. The thinnest and the thickest spots on the slit samples shall be avoided. The average of these eight measurements shall be used to determine the average coating thickness.

The holes from which slit samples were taken shall be filled with a nonflammable caulk or sealant.

Weight or volume of the coating applied to the entire module area in (lb/ft2 or gallons/ft2) shall be recorded along with the measured DFT.

Method 2 (Medallion/target method). Where Method 2 is used, two metal medallions shall be installed within 24 inches (610 mm) of the corner where the burner is to be placed. The medallions shall be a minimum of 2 inches by 2 inches (51 mm by 51 mm) with a 1/4-inch-diameter (6.4 mm) hole in the center and a nail or screw shall be installed in the hole to fasten the medallion to the foam surface.

The coating thickness (dry mils film thickness) shall be measured at four random locations of each medallion sample using an optical comparator or caliper. The thinnest and the thickest spots on the samples shall be avoided. The average of these eight measurements shall be used to determine the average coating thickness.

The bare spots on the foam where the medallions were removed shall be coated with nonflammable caulk, coating or sealant prior to conducting the test.

302.4.1.2 Test corner configuration. The installation of the spray-applied foam plastic insulation shall be provided as a smooth  surface, with attention in the wall areas that will be adjacent to and above the burner. The maximum allowable deviations shall be in accordance with Figure 1.

302.4.1.2.1 Test data. During the test, the test parameters in Items 1 through 4 shall be determined:

1.	Time at which the Heat Release Rate exceeds 1 MW.

2.	Time at which the heat flux to the floor exceeds 20 kW/m2.

3.	Time at which the average upper layer temperature exceeds 600ºC.

4.	Time at which flames exit the doorway.

302.4.1.2.2 Test report. In addition to the requirements for reporting stated in NFPA 286, Items 1 through 4 shall be reported:

1.	Type, description, average thickness and nominal density of the spray-applied foam plastic insulation wall and ceiling specimens.

2.	The type, description, and nominal thickness (in mils) or application rate (in gallons per 100 square feet) of coating, if used as part of the insulation system.

3.	Time recorded for each test parameter from Section 302.4.1.2.1.

4.	Average of the four-time values indicated in Section 302.4.1.2.1.

302.4.1.2.3 Conditions of acceptance. Each test shall have an average time for attainment of the four measured test parameters specified in Section 302.4.1.2.2, Item 4, of 4 minutes 18 seconds or greater.

Note: This condition of acceptance is based on comparison of results for the tested assembly versus results for a code-prescribed ignition barrier applied over foam plastic insulation.

302.4.1.2.4 Attic installation limitations. Where testing is in accordance with Section 302.5.1, Conditions 1 through 8 regarding installation under the International Building Code or the International Residential Code shall apply.

1.	Entry to the attic shall only be to service utilities, and no storage is permitted.

2.	There shall be no interconnected attic areas.

3.	Air in the attic shall not be circulated to other parts of the building.

4.	Attic ventilation is provided where required by  Section 1203.2 of the International Building Code or Section R806 of the International Residential Code, except where air impermeable insulation is installed in unvented attics in accordance with the Section 1203.3 of the International Building Code or Section R806.5 of the International Residential Code.

5.	The foam plastic insulation shall be limited to the maximum thickness and density tested.

6.	Combustion air is provided in accordance with Section M1701 of the International Residential Code, where applicable.

7.	The installed coverage rate or thickness of coatings, where part of the insulation system, shall be equal to or greater than that which was tested.

8.	An installation certificate with the following information shall be posted at each entrance:

- Product name and installation thickness.  Coating product name, installation rate, wet film thickness and dry film thickness, if applicable.

- Manufacturer name, address and contact information

- Installation contractor name, address and contact information

- Attestation that the product(s) have been installed in accordance with the manufacturer’s installation instructions and the requirements of the evaluation report.

- A notice that the certificate is not to be removed or altered.

- A list of limitations for the space including the following:

  - Entry to the space is only to service utilities, and no storage is permitted.

  - FIRE SAFETY WARNING: If hot work (welding / cutting) is required to be performed, all necessary procedures, precautions and limitations must be observed in accordance with OSHA 1926 Subpart J Standard 1926.352 requirements for hot work performed in the vicinity of combustible materials.

302.4.1.2.5 Attic floors. Where Test Method A is used to qualify the use of the spray-applied foam plastic on attic floors, the maximum thickness shall be based on the maximum thickness applied on the walls. Where the testing incorporates a covering or coating used on the test walls, it shall also be required for the attic floor application.

302.4.2 Test Method B. Where Test Method B is used, tests shall be conducted in accordance with NFPA 286 with the conditions of acceptance specified in Section 803.1.2.1 of the International Building Code, or UL 1715 with conditions of acceptance as specified in Section 302.4.2.1. The reported thickness shall be in accordance with Figures 2 and 3. Placement of the burner or wood crib shall be in accordance with the standard being used for testing, with the measured distance between the burner or crib and the interior surface of the assembly as described in Figure 1.

302.4.2.1 Attic installation limitations. Where testing is in accordance with Section 302.4, Conditions 1 through 4 regarding installation under the International Building Code or International Residential Code shall apply.

1.	Attic ventilation is provided when required by Section 1203.2 of the International Building Code or Section R806 of the International Residential Code.

2.	The foam plastic insulation shall be limited to the maximum thickness and density tested.

3.	Combustion air is provided in accordance with Section M1701, where applicable.

4.	The installed coverage rate or thickness of coatings, if part of the insulation system, shall be equal to or greater than that which was tested.

302.4.3 Attic floors. Where Test Method B is used to qualify the use of the spray-applied foam plastic on attic floors, the maximum thickness shall be based on the maximum thickness applied on the ceiling. Where the testing incorporates a covering or coating used on the test walls, it shall also be required for the attic floor application.

    - 302.4.3.1 Attic floors only. Where the insulation is installed on the attic floor only without a prescriptive ignition barrier, the prescribed ignition barrier shall not be required when the exposed spray-applied foam plastic or spray-applied foam plastic with a covering  is tested in accordance with ASTM E970, where the measured critical radiant flux is equal to or greater than 0.12 watt per square centimeter. The initial sample shall be thick enough that upon completion of the ASTM E970 test, at least 1/2 inch (12.7 mm) of the foam thickness remains across the entire sample panel. Consistent thickness and flatness of the specimen surface shall be established by taking three foam thickness measurements using a 3-inch (76 mm) disk-pin probe. The measurements shall be taken along the centerline of the specimen at 1/4L, 1/2L, and 3/4L from the end of the specimen, where L is the length of the test specimen. These three thickness measurements shall not deviate by more than 1/2 inch (12.7 mm). The maximum thickness of foam plastic shall be the foam plastic thickness applied to the ceiling of room test modules tested in accordance with Section 302.4.1 or 302.4.2.

    - 302.4.4 Test Method U. Where the test method U is used as an alternative method of qualifying spray foam plastic installation for use in unvented attic spaces, testing shall be carried out in accordance with Section 302.4.4.1- Section 302.4.4.2.1.8.

    - 302.4.4.1 Scope. Where Test Method U is used to qualify spray foam plastic installation, approval shall be limited for use in unvented attic spaces only.

      - 302.4.4.1.1 General:.	The objective of this testing is to evaluate the fire performance of spray-applied foam plastic insulation  (SPF) materials where tested in a modified room corner test configuration to determine if the insulation and/or the insulation system is acceptable for use on walls and the underside of roof sheathing in unvented attics without prescriptive ignition barriers required under the IRC or IBC.  This testing is limited to spray-applied foam plastic insulation materials that have been evaluated as air impermeable insulation in accordance with Section 302.2.1 and that have also demonstrated a flame-spread index of 25 or less and a smoke-developed index of 450 or less in accordance with Section 302.2.2.

      - 302.4.4.1.2 Use in Unvented Attics:.	Spray-applied polyurethane foam plastic insulation installed in unvented attics where entry is made only for service of utilities shall be protected by an ignition barrier as set forth in IBC Section 2603.4.1.6, and IRC Section R302.5.3.

      - 302.4.4.2 Ignition Barrier. The prescriptive ignition barrier shall not be required where satisfactory testing is conducted with exposed foam plastic insulation or with a foam plastic insulation system covered by a coating in accordance with the following:

        - 302.4.4.2.1 Test Method:. The test procedure shall be in accordance with NFPA 286 with the modifications described below.

          - 302.4.4.2.1.1 Ignition Source. The standard NFPA 286 gas burner shall be used. The burner shall be positioned in the test corner of the fire test room as indicated in Figure 1.

        - 302.4.4.2.1.2 Specimen Mounting. The room shall be constructed, and the test specimens shall be mounted in the configuration described below. The interior room dimensions after specimen mounting, as required by the NFPA 286 test procedure, shall be maintained. See Figure 4 for additional information.

          - 302.4.4.2.1.2.1 Room Construction. The four walls, attic floor and roof of the test room shall be constructed with minimum nominal 2 by wood studs / joists spaced 24 inches (610 mm) on center; the walls of the room shall be constructed with a single top and bottom plate. A total of five attic floor joists and five roof joists shall be used; the joists shall run parallel with the interior 12-foot length (3.6 m) of the test room. The two outboard roof joists shall rest on the top plates of the walls.  The length of the wall studs, roof joists and attic floor joists will vary based on the thickness of SPF to be tested; the room shall be framed such that the interior volume of the room is 768 cubic feet (21.75 cubic meters) +/- 5% after spraying the SPF. The exterior side of the walls and roof shall be covered with one layer of 15/32-inch-thick (11.9 mm), code compliant wood structural panel sheathing. The attic floor shall be covered with one layer of 1/2”-inch-thick (12.7 mm) gypsum board attached to the bottom side of the joists; the gypsum board on the underside of the attic floor shall be fastened in accordance with Table R702.3.5 of the IRC and finished to a Level 2 finish in accordance with ASTM C840. A 22”x30” opening shall be provided in the location shown in Figure 5; the opening shall remain unobstructed during the test.

Thermocouples shall be placed around the opening as shown in Figure 5.

          - 302.4.4.2.1.2.2 SPF Application. The SPF shall be sprayed to fill each stud cavity and be continuous from the bottom plate to the top plate and from stud to stud. The SPF shall be sprayed to fill each roof joist cavity and shall be continuous from the front to the back and from joist to joist.  Where a coating (e.g., intumescent coating) is used over the foam, it shall be applied to both the walls and the ceiling at the same minimum thickness or coverage rate intended for use.

- Where a coating is used over the foam, its thickness shall be measured in accordance with Section 302.4.1.1.

          - 302.4.4.2.1.2.3 Room Mounting and Equipment Configuration. The test room shall be elevated approximately 45” to 48” (1.14 to 1.22 m) above the ground to allow access and observation from below.  The means of support shall be determined by the test laboratory. Two viewing ports shall be provided with ¼ in. thick, heat-resistant glass.  The ports shall be not greater than 144 in.2 and shall be provided such that the burner and the attic ceiling is observable at the start of the test.  Three sides of the test room and two sides of the smoke collection hood shall be skirted with a minimum of ½ inch thick gypsum panels directing the smoke towards the hood as shown in Figure 6.  The skirts shall extend from the bottom of the test room and smoke collection hood to the floor.  The joints between the skirt boards shall be taped, and gaps between the bottoms of the panels and the floor shall be sealed.  Thermocouples and radiometer within the room shall be placed in the locations prescribed in NFPA 286, except the thermocouple that is prescribed to be located over the conventional door opening shall be placed 12 inches (355 mm) above the burner. Eight additional thermocouples shall be installed below the hatch opening, 12 inches (355 mm) below the opening, two per side equally spaced.  All thermocouples and radiometer are shown in Figure 7.

        - 302.4.4.2.1.3 Test Corner Configuration. During the installation of the SPF, the surface shall be smooth  with notice in the wall areas adjacent to and above the burner. The maximum deviations are described in Figure 1.

        - 302.4.4.2.1.4 Initial Test Period. The test shall be conducted for the first 15 minutes at one second intervals.

        - 302.4.4.2.1.5 Observation Period After Flame Extinguishment.  Once the fire has been extinguished in accordance with section 302.4.4.2.1.6 f, the room shall be continuously monitored for 5 hours for reignition.  During the observation period and after the initial 15 minutes, the data from the thermocouples shall be continuously recorded at intervals no greater than 15 seconds.  After the 5-hour observation period, the test may be terminated.

    - 302.4.4.2.1.6 Test Data.  The following test parameters shall be recorded throughout the test:

- Time at which the SPF ignites shall be noted as the start of the test.

- Heat flux in the center of the attic floor shall be measured. Temperatures in the attic ceiling shall be measured.

- Video documentation of the test shall be recorded in one of the observation ports and underneath the attic assembly to record flaming out of the hatch opening.

- Time at which flames exit the hatch opening and the duration in which flames exit the hatch opening. Post-test video shall be reviewed for confirmation.

- Time at which total smoke released exceeds 1,000 m2. Post-test data shall be used to confirm.

- Time at which any thermocouple on the exterior of the attic hatch exceeds 527ºC (980 ºF).

- Time at which the fire extinguished.

- Extinguishment of the fire is determined via monitoring the thermocouple placed 305 mm (12 inches) above the burner.  Once the temperature reading has decreased below 482ºC (900 ºF), the fire can be considered extinguished at the burner, and the gas should be turned off.

- Determination of whether or not reignition of test assembly occurs during 5-hour observation period.

          - 302.4.4.2.1.7 Report. The following additional items shall be reported

- Type, description, average thickness and nominal density of the SPF applied to the walls and ceiling.

- Where used as part of the insulation system, the type, description, and nominal thickness (in mils) or application rate (in gallons per 100 square feet) of coating.

- Time recorded for each test parameter from Section. 3.03.4.4.2.1.6 above.

    - 302.4.4.2.1.8Conditions of Acceptance. A test shall be determined to be successful when all of the following conditions have been met:

- The total smoke released shall not exceed 1,000 m2.

- The duration of sustained flaming out of the attic hatch shall not exceed 10 seconds.

- Thermocouples at the attic hatch opening shall not stay elevated above 527 ºC (980 ºF) for more than 5 seconds.

- The fire shall extinguish in less than or equal to 60 seconds from the start of the test (see section 302.4.4.2.1.6 a).

- Reignition during the 5-hour observation period shall not occur.

        - 302.4.4.2.2 Alternative Breakaway Scuttle Hatch Attic Entry (Optional). Scuttle hatches with removable panels, such as gypsum board, used as an alternative to downward opening hatches shall be evaluated in accordance with this section.  Note: in order to be evaluated in accordance with this section, the panels shall meet the Class A interior finish requirements outlined in IBC Section 803.1.2, (2015, 2012 and 2009 IBC Section 803.1.1 or 2006 IBC Section 803.1) where tested in accordance with ASTM E84 or UL 723.

          - 302.4.4.2.2 .1Test Method. Three replicate panels measuring a minimum of 22 inches by 30 inches (55.9 cm by 76.2 cm) shall be loaded to failure in accordance with the uniform loading procedures outlined in Section 11 of ASTM E72.  The panels shall be simply supported on all four sides.  The bearing width of the panels on the supports shall be the maximum bearing width to be described in the evaluation report.

          - 302.4.4.2.2.2 Conditions of Acceptance. The average ultimate uniform load shall be less than or equal to 10 psf. The evaluation report shall include the minimum panel size and maximum bearing width evaluated.

          - 302.4.4.2.2.3 Increased Uniform Load. Where the average ultimate uniform load is increased to 20 psf, the associated statement in Section U2.3.h.ii regarding the design of the interior surfaces of the attic shall be included in the evaluation report.

        - 302.4.4.2.3 Limitations. Spray applied foam plastic installation qualified for use without an ignition barrier will be subject to the limitations found in 302.4.4.2.3.1.

    - 302.4.4.2.3.1 Attic Installation. Where testing is in accordance with 302.4.4, the evaluation report shall include the following limitations:

- Entry to the attic is only to service utilities, and no storage is permitted.

- There are no interconnected attic areas.

- Air in the attic is not circulated to other parts of the building.

- The foam plastic insulation is limited to the maximum thickness and density tested.

- Combustion air is provided in accordance with IMC Section 701 or 2006 IMC Sections 701 and 703.

- The installed coverage rate or thickness of coatings, if part of the insulation system, shall be equal to or greater than that which was tested.  When a coating is used, the evaluation report shall specify the minimum wet film thickness, dry film thickness and application rate, as applicable.

- Where hot work is required to be performed, all necessary procedures, precautions and limitations must be observed in accordance with OSHA 1926 Subpart J Standard 1926.352 requirements for hot work (welding / cutting) performed in the vicinity of combustible materials.

- One of the following limitations shall be provided regarding the attic hatch(es):

    - For systems that do not include evaluation in accordance with section 302.4.4.2.2: A downward opening attic hatch is required.  The hatch shall remain closed at all times except for when servicing of utilities is required.  The hatch shall be able to be opened freely without disengaging a latching or locking mechanism.

    - For systems that include evaluation in accordance with Section 302.4.4.2.2: A downward opening attic hatch or breakaway scuttle hatch is required [a description of the breakaway scuttle hatch panel including panel thickness, minimum panel dimensions, and support conditions (maximum bearing width) shall be provided].  The hatch shall remain closed at all times except for when servicing of utilities is required.  The hatch shall be able to be opened freely without disengaging a latching or locking mechanism.

        - For systems that include evaluation in accordance with the exception to Section U2.2.2, the following statement shall also be included: “For installations with a breakaway scuttle hatch, all interior surfaces of the attic, including the floor, roof and walls must be designed to resist outward uniform loads greater than or equal to 20 psf. Evidence of compliance with these design requirements must be prepared by a registered design professional and submitted to the local code official where required by the statutes of the jurisdiction in which the project is to be constructed.”

- The maximum uniform pressure required to open the downward opening attic hatch shall be less than or equal to 10 psf.  The performance of the downward opening attic hatch is outside of the scope of the evaluation report, but adequate information shall be provided to the local code official to demonstrate that this requirement has been satisfied.  For field verification, the force required to open the downward opening hatch, when measured from the edge of the downward opening hatch opposite the hinges shall not exceed the value calculated using the equation below.

- An installation certificate with the following information shall be posted at each entrance:

  - Product name and installation thickness. Coating product name, installation rate, wet film thickness, and dry film thickness, if applicable.

  - Manufacturer name, address, and contact information.

      - - Name, address, and contact information for installer.

  - Attestation that the product(s) have been installed in accordance with the manufacturer’s installation instructions and the requirements of the evaluation report.

  - A notice that the certificate is not to be removed or altered.

  - A list of limitations for the space including the following:

- Entry to the space is only to service utilities, and no storage is permitted.

- The hatch shall remain closed at all times except for when servicing of utilities is required.  No locks or latches that would prevent the hatch from opening freely may be added to the hatch.

- FIRE SAFETY WARNING: If hot work (welding / cutting) is required to be performed, all necessary procedures, precautions and limitations must be observed in accordance with OSHA 1926 Subpart J Standard 1926.352 requirements for hot work performed in the vicinity of combustible materials.

- Notification that the space has been designed and constructed / installed as an unvented attic assembly; introduction of any penetrations to the exterior or alterations to the insulation shall be designed by a registered design professional.  The design of the change shall be submitted to the local code official for approval, as required by the local jurisdiction.

302.5 Testing for alternative ignition barrier assembly for use in crawl spaces.

Where the spray-applied foam plastic insulation is intended to be installed as a component of an alternative ignition barrier assembly (i.e., without a code-prescribed ignition barrier), the assembly shall be qualified by testing as specified in either Section 302.6.1 (Test Method C) or 302.6.2 (Test Method D) of this standard or in the Special Approval section of the International Building Code or the Specific Approval section of the International Residential Code. The requirements of this section apply to both an exposed spray-applied foam plastic insulation or to a spray-applied foam plastic insulation system using a covering.

302.5.1 Test Method C. Where Test Method C is used, testing shall be conducted as set forth in Section 302.5.1.

302.5.1.1 Crawl space installation limitation. Where testing is in accordance with Section 302.6.1, Conditions 1 through 7 regarding installation under the International Building Code or the International Residential Code shall apply.

1.	Entry to the crawl space shall only be to service utilities, and no storage is permitted.

2.	There shall be no interconnected crawl space areas.

3.	Air in the crawl spaces shall not be circulated to other parts of the building.

4.	Under-floor (crawl space) ventilation is provided when required by Section 1203.3 of the International Building Code or Section R408.1 of the International Residential Code, as applicable.

5.	The foam plastic insulation shall be limited to the maximum thickness and density tested.

6.	Combustion air is provided in accordance with IMC Section M1701, where applicable.

7.	The installed coverage rate or thickness of coatings, if part of the insulation system, shall be equal to or greater than that which was tested.

Use of the spray-applied foam plastic insulation in an unvented crawl space is limited to testing in accordance with Section 302.6.1.2.1 (Option 1), or application with a code-prescribed ignition barrier.

302.5.1.2 Test Method D. Where Test Method D is used, testing shall be performed in accordance with Section 302.6.1.2.1 (Option 1) or Section 302.6.1.2.2 (Option 2).

302.5.1.2.1 Testing (Option 1). Tests shall be conducted in accordance with NFPA 286 with the conditions of acceptance specified in Section 803.1.2.1 of the International Building Code; or UL 1715 with conditions of acceptance as specified in Section 302.4.2.1. The reported thickness shall be in accordance with Figures 2 and 3. Placement of the burner or wood crib shall be in accordance with the standard being used for testing, with the measured distance between the burner or crib and the interior surface of the assembly as described in Figure 1.

302.5.1.2.1.1 Crawl space installation limitations. Where testing is in accordance with Section 302.6.1.2.1, limitations 1 through 4 on installation shall apply:

1.	Under-floor (crawl space) ventilation shall be provided in accordance with Section 1203.3 of the International Building Code or Section R408 of the International Residential Code, as applicable.

2.	Combustion air shall be provided in accordance with Section 701 of the International Mechanical Code, where applicable.

3.	The foam plastic insulation shall be limited to the maximum thickness and density tested.

4.	The installed coverage rate or thickness of coatings, if part of the insulation system, shall be equal to or greater than that which was tested.

302.5.1.2.2 Testing (Option 2). Comparative crawl space fire tests shall be conducted in accordance with this section to compare the performance of the exposed spray-applied foam plastic insulation under identical test conditions as described in Sections 302.6.1.2.2.1 through 302.6.1.2.2.6 to that of the spray-applied foam plastic insulation covered with a prescriptive ignition barrier.

302.5.1.2.2.1 Test configuration. A subfloor assembly shall be mounted on top of a three- sided wall module. The simulated crawl space module shall consist of three 8-foot square (0.74 m2) [outside dimensions ± 2 inches (51 mm)] walls, each 48 ± 2 inches (1219 mm ± 51 mm) high, and built of nominal 4-inch-wide (102 mm) by 8-inch-high (203 mm) by 16-inch-long (406 mm) concrete blocks with a full open space on one side of the structure. Masonry walls or module walls constructed of wood or metal studs with two layers of 1/2 inch (12.7 mm) gypsum board are not prohibited where the interior dimensions are the same as for a concrete block module, i.e., 88 ± 2 inch-wide (2235 mm ± 51 mm) and 92 ± 2 inch-deep (2337 mm ± 51 mm). Where wood or metal stud construction is used, the studs shall be located inside the module, i.e., the width of the module is equal to the distance between the interior faces of the gypsum board attached to the side walls and the depth is equal to the distance between the front opening and the interior face of the gypsum board attached to the back wall.

The floor/ceiling above the crawl space shall be built using nominal 2-inch by 8-inch by 8-foot (2.4 m) floor joists on 16-inch (406 mm) centers, with 2-inch by 8-inch or deeper joist headers, all bearing on 2-inch by 4-inch sill plates and surfaced with 15/32-inch-thick (12 mm), 4-ply, APA graded A-C plywood sub-flooring.

Construction lumber including joists and studs where usedshall be of the same species and grade for tests conducted to qualify the spray-applied foam plastic insulation.

The joists shall be oriented perpendicular to the camera’s line-of-sight. The floor of the test chamber shall be covered with approximately 1 inch (25.4 mm) of sand. As an option, additional floor covering with 1/2 inch (12.7 mm) gypsum board before installing the 1-inch (25.4 mm) layer of sand shall be used.

302.5.1.2.2.2 Ignition source. The fire source shall be a 22-lb (9.9 kg) wood crib constructed of nominal 2-inch by 2-inch No. 1 select grade white pine (no knots), 15-inch square (9677 mm2) in plan, spaced approximately 11/2-inch (38 mm) apart and fastened at right angles with a single nail at each end ± 0.5%. The crib shall be placed in a rear corner of the crawl space 1 inch (25.4 mm) from each wall surface and supported approximately 4 inch (102 mm) above the floor on small sections of refractory brick. The crib sticks of the bottom layer shall be parallel to the side walls.

Approximately 150 ml of ethyl alcohol in a circular or square metal pan with a surface area of 36 to 40 in2 (23226 to 25806 mm2) placed under the crib shall be used for ignition.

302.5.1.2.2.3 Test duration and end point comparison criteria. The following Items 1 and 2 shall be measured and reported:

1.	Time to flames emerging from the front of the crawl space.

2.	Time to burn-through of the floor/deck system. If burn-through is not reached prior to laboratory personnel ending the test, the time at which the test was ended and reason for ending the test shall be reported.

302.5.1.2.2.4 Documentation. The test shall be recorded with photographs and video documentation positioned to view the front of the open side of the module. A timing reference, mechanical or electronic, shall be included in the photographic and video records.

302.5.1.2.2.5 Test report. The report shall include the following Items 1 through 6:

1.	Name and location of facility where test is conducted.

2.	A description of the tested assembly with emphasis on the insulation type (including facings), thickness, density and attachment details.

3.	Photographic and video documentation: pre-test, during (including timing) and post-test.

4.	A summary of visual observations including time to flames exiting the module and/or burn through of the subfloor.

5.	Conclusions in the form of a statement of findings summarizing the fire performance of the assembly; and, as appropriate, compared to a control assembly.

6.	Signature of a representative engineer or officer of the test facility.

302.5.1.2.2.6 Installation limitations. Where testing is in accordance with this section, the following limitations 1 through 8 regarding use and installation shall apply:

1.	Entry to the crawl space is only to service utilities and no storage is permitted.

2.	There are no interconnected crawl space areas.

3.	Air in the crawl space is not circulated to other parts of the building.

4.	Under-floor (crawl space) ventilation is provided, when required by Section 1203.3 of the International Building Code or Section R408 of the International Residential Code, as applicable.

5.	The foam plastic insulation is limited to the maximum thickness and density tested.

6.	Combustion air is provided in accordance with Section M1701 of the International Mechanical Code, where applicable.

7.	The installed coverage rate or thickness of coatings, if part of the insulation system, shall be equal to or greater than that which was tested.

8.	An installation certificate with the following information shall be posted at each entrance:

- Product name and installation thickness.  Coating product name, installation rate, wet film thickness and dry film thickness, if applicable.

- Manufacturer name, address and contact information

- Installation contractor name, address and contact information

- Attestation that the product(s) have been installed in accordance with the manufacturer’s installation instructions and the requirements of the evaluation report.

- A notice that the certificate is not to be removed or altered.

- A list of limitations for the space including the following:

•  Entry to the space is only to service utilities, and no storage is permitted.

•  FIRE SAFETY WARNING: If hot work (welding / cutting) is required to be performed, all necessary procedures, precautions and limitations must be observed in accordance with OSHA 1926 Subpart J Standard 1926.352 requirements for hot work performed in the vicinity of combustible materials.

302.6 Use on sill plates and headers without a code-prescribed thermal barrier. Where the spray-applied foam plastic insulation is to be installed in Type V construction on sill plates and headers without a code prescribed thermal barrier, the spray-applied foam plastic insulation assembly shall comply with either Section 302.10.1 or Section 302.10.2.

302.6.1 Code Limitations. The spray-applied foam plastic insulation shall comply with the requirements outlined in Section 2603.4.1.13 of the International Building Code or Section 316.5.11 of the International Residential Code as listed below:

- The maximum thickness of the spray-applied foam plastic insulation shall be 31/4 inches (82.6 mm).

- The density of the spray-applied foam plastic insulation shall be 0.5 to 2.5 pcf (24 to 32 kg/m3).

- The foam plastic shall have a flame spread index of not greater than 25 and an accompanying smoke-developed index of not greater than 450 where tested in accordance with ASTM E84 or UL 723.

302.6.2 Application at Greater Thickness. For spray-applied foam plastic insulation that does not comply with the requirements of Section 302.9.1, a room corner test in accordance with NFPA 286 with the modifications described in this section shall be conducted.

302.6.3 Test configuration.  The three walls of the test room without the doorway shall be constructed with wood studs, 93 inches high (236 mm), 24 inches (610 mm) on center, with a single top and bottom plate. The top 6 inches (152.4mm), minimum of the studs shall be notched to the thickness of spray-applied foam plastic insulation to be tested (See Figure 8).  The framing for the ceiling and the wall with the doorway of the test room shall be constructed in accordance with the NFPA 286 test procedure. Excluding the notched cavity at the top of the wood studs, the fire test room shall be completely lined with one layer of 5/8-inch thick (15.9 mm) Type X gypsum wall board covered by one layer of 1/4-inch thick (6.4 mm) cement board.  The notched cavity at the top of the wood studs shall be lined with one layer of 1/4-inch thick (6.4mm) cement board.  The SPF shall be sprayed to fill the notched cavity and will be continuous (see Figure 8). Where a coating (e.g., intumescent coating) is used over the foam, it shall be applied to the SPF at the same minimum coating thickness or coating coverage rate intended for use. Refer to Figure 8.  Where a coating is used, its thickness shall be measured as outlined in Section 302.5.1.1 of this standard.

302.6.4 Test report. In addition to the requirements for reporting stated in NFPA 286, Items 1 through 3 shall be reported:

1.	Type, description, average thickness and nominal density of the spray-applied foam plastic insulation specimens.

2.	The type, description, and nominal thickness (in mils) or application rate (in gallons per 100 square feet) of coating, if used as part of the insulation system.

3.	The observation section of the test report shall document that the test flame reached the exposed spray-applied foam plastic insulation, or the exposed coated spray-applied foam plastic insulation, and the distance of lateral (horizontal) flame spread to the outer extremity of each wall. If the flame front does not reach the cavity height, the testing shall be repeated until the flame front impinges upon the spray-applied foam plastic insulation filled cavity.

302.6.5 Conditions of acceptance. Conditions of acceptance shall be specified in International Building Code Section 803.1.1.1 (2015, 2012 and 2009 International Building Code Section 803.1.2.1; 2006 International Building Code Section 803.2.1) or International Residential Code Section R302.9.4, as applicable.

302.6.6 Installation limitations.  Where testing is in accordance with Section 302.10, Conditions 1 through 3 regarding installation under the International Building Code or the International Residential Code shall apply.

1. The foam plastic insulation is limited to the maximum thickness and density tested.

2. The installed coverage rate or thickness of coatings, if part of the insulation system, must be equal to or greater than that which was tested.

3. Use is limited to Type V construction on sill plates and headers when the spray-applied foam plastic insulation is installed without a code-prescribed thermal barrier.

302.7  Exterior walls of Types I, II, III and IV construction (International Building Code). Where the spray-applied foam plastic insulation is intended for use in certain construction types defined in Section 602 of the International Building Code where noncombustible materials are required, the spray-applied foam plastic insulation shall be qualified for use in exterior walls of construction Types I, II, III and IV by testing in accordance with this section provided the results of testing meet criteria according to Section 2603.5 of the International Building Code. In addition, where the exterior wall is required to have a fire-resistance rating, the testing requirements of Section 302.7 shall apply.

302.7.1 Vertical and lateral fire propagation. Testing of the specific wall assembly shall be conducted in accordance with NFPA 285. The NFPA 285 test reports shall include details of the assembly tested.

302.7.2 Potential heat. The potential heat content of the spray-applied foam plastic shall be determined by testing performed in accordance with NFPA 259.

302.7.3 Ignition properties. Where required by the building code, the ignition properties of wall assemblies incorporating spray-applied foam plastic shall be determined by testing conducted in accordance with NFPA 268.

302.7.4 Use in fire-resistance-rated construction. Where spray-applied foam plastic insulation is installed as a component of a fire-resistance-rated assembly, testing of the assembly that incorporates the spray-applied foam plastic insulation shall be conducted in accordance with ASTM E119 or UL 263 for the hourly rating intended for use.

302.8 Roofing applications.

302.8.1 Use in roofing applications. Where the spray-applied foam plastic insulation is used in roofing applications, the testing specified in Sections 302.8.2 through 302.8.4 shall be performed.

302.8.2 Physical properties. Spray-applied foam plastic insulation used in roofing applications shall comply with the physical property requirements of Table 3 or ASTM C1029, Type III or IV, or ASTM D7425, as applicable.

302.8.3 Surface-burning characteristics tests.

302.8.3.1 Flame-spread index. The insulation shall exhibit a flame-spread index not greater than  75 where tested in accordance with ASTM E84 or UL 723 at the maximum thickness and density intended for use, but no greater than 4 inches (102 mm).

302.8.3.2 Smoke-developed index. Testing to determine the smoke-developed index shall be waived for roofing application under Section 2603.3 (Exception 3) of the International Building Code and Section R316.5.2 of the International Residential Code.

302.8.4 Roof classification. Spray-applied foam plastic insulation used in roofing applications shall comply with Sections 1507.14 and 2603.6 of the International Building Code or Sections R902 and R905.14 of the International Residential Code, as applicable. Fire classification of roof coverings with spray-applied foam plastic insulation shall be based on testing in accordance with ASTM E108 or UL 790 and Section 1505 of the International Building Code.

302.8.5 Installation requirements. Installation of spray-applied foam plastic insulation in roofing applications shall be in accordance with the requirements of Section 303.1.2.1.

302.9	Spray applied foam plastic sealants .

302.9.1  Use. Spray applied foam plastic sealants shall meet the performance requirements laid out in Table 4. Spray applied foam plastic sealants typically are used in minor amounts to fill  small cracks and gaps, and to make minor repairs. Spray applied foam plastic sealants used in this manner shall be used in accordance with manufacturer’s instructions.

SECTION 303
INSTALLATION

303.1 Installation requirements. Installation of spray-applied foam plastic insulation shall comply with the requirements of Sections 303.1.1 through 303.5, as applicable to the end use application.

303.1.1 General requirements. Installation of spray-applied foam plastic insulation shall not exceed the thickness and density as tested in accordance with Section 302.2, except where stated otherwise in this standard. Where separated from the interior of the building by a prescriptive thermal barrier, the spray-applied foam plastic insulation when tested under Section 302.2 at 4-inch (102 mm) thickness with flame-spread index no greater than 25 and smoke-developed index no greater than 450 shall be limited to maximum density tested, but shall have no maximum thickness limitation.

303.1.2 Wall and floor installation thermal barrier requirements. Installation of spray-applied foam plastic insulation in wall and floor applications shall be separated from the interior of the building as set forth in Section 2603.4 of the International Building Code, Section R316.4 of the International Residential Code, as applicable, except when qualified in accordance with Section 302 as applicable.

303.1.2.1 Roofing application thermal barrier requirements. Installation of spray-applied foam plastic insulation in roofing applications shall be separated from the interior of the building as set forth in Section 2603.4.1.5 of the International Building Code or Section R316.5.2 of the International Residential Code, as applicable.

303.2 Use in attics.

303.2.1 Thermal barrier.

Exception: Within an attic where entry is made only for service of utilities, spray-applied foam plastics shall be protected by a prescriptive ignition barrier in accordance with Section 2603.4.1.6 of the International Building Code or Section R316.5.3 of the International Residential Code, as applicable, or qualified as a component in an alternative ignition barrier assembly in accordance with Section 302.4.  Where qualified in accordance with Section 302.4.1 (Method A) or Section 302.4.3 (Method U ), installation certificate(s) shall be provided by the installer as outlined in Section 302.4.1.2.4(8); the certificate(s) shall be red in color and constructed of durable materials such as metal, plastic or laminated paper

303.2.2 Unvented attic requirements under the 2018 and 2015 International Building Code and 2018, 2015, 2012, 2009, and 2006 International Residential Code. Installation of spray-applied foam plastic insulation in unvented attics shall be qualified in accordance with the conditions prescribed in Section 1203.3 of the International Building Code or Section R806.5 of the 2015 International Residential Code [2009 IRC Section R806.4], and where tested in accordance with Section 301.3.

303.3 Use in crawlspaces.

303.3.1 Thermal barrier.

Exception: Installation of spray-applied foam plastic insulation in a crawl space where entry is made only for service of utilities, spray-applied foam plastic shall be protected by a prescriptive ignition barrier in accordance with Section 2603.4.1.6 of the International Building Code or Section R316.5.4 of the International Residential Code, as applicable, or qualified as a component in an alternative ignition barrier assembly in accordance with Section 302.6. Where qualified in accordance with Section 302.6.1.2.2 (Method D; Option 2), installation certificate(s) shall be provided by the installer as outlined in Section 302.6.1.2.2.6(8); the certificate(s) shall be red in color and constructed of durable materials such as metal, plastic or laminated paper

303.3.2 Unvented crawl spaces under the International Residential Code. Installation of spray-applied foam plastic insulation in unvented crawl spaces shall be qualified in accordance with the conditions prescribed in Section R408.3 of the International Residential Code and Sections 301.3. The foam plastic insulation shall be protected from fire in accordance with IRC Section R316.4, as applicable to the air exchange or conditioning method used for the crawl space.

303.4 Use in exterior walls of buildings of Type I, II, III or IV construction (International Building Code). Installation of spray-applied foam plastic insulation in or on exterior walls of building Types I, II, III and IV shall comply with the requirements of Section 2603.5 of the International Building Code and shall be qualified in accordance with the requirements of Section 302.7.

CHAPTER 4

REFERENCED STANDARDS

(See Appendix A – Codes and Referenced Standards Correlation Table for additional information)

ASTM

ASTM International

100 Barr Harbor Drive, P.O. Box C700

West Conshohocken, PA 19428-2959

ASTM C177

Test Method for Steady-State Heat Flux Measurements and Thermal Transmission Properties by Means of the Guarded Hot Plate Apparatus

ASTM C208

Standard Specification for Cellulosic Fiber Insulating Board

ASTM C518

Test Method for Steady-State Heat Flux Measurements and Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus

ASTM C1029

Specification for Spray-Applied Rigid Cellular Polyurethane Thermal Insulation

ASTM C1363

Standard Test Method for Thermal Performance of Building Materials and Envelope Assemblies by Means of a Hot Box Apparatus

ASTM D1621

Test Method for Compressive Properties of Rigid Cellular Plastics

ASTM D1622

Test Method for Determining Apparent Density of Rigid Cellular Plastics

ASTM D1623

Test Method for Tensile and Tensile Adhesion Properties of Rigid Cellular Plastics (Type B Specimen)

ASTM D2126

Test Method for Response of Rigid Cellular Plastics to Thermal and Humid Aging

ASTM D6226

Standard Test Method for Open-Cell Content of Rigid Cellular Plastics

ASTM D7425

Standard Specification for Spray Polyurethane Foam Used for Roofing Applications

ASTM E84

Test Methods for Surface Burning Characteristics of Building Materials

ASTM E96

Test Method for Water Vapor Transmission of Materials

ASTM E108

Test Method for Fire Tests of Roof Coverings

ASTM E119

Test Methods for Fire Tests of Building Construction and Materials

ASTM E283

Test Method for Determining the Rate of Air Leakage through Exterior Windows Curtain Walls and Doors under Specified Pressure Differences across the Specimen

ASTM E970

Test Method for Critical Radiant Flux of Exposed Attic Floor Insulation Using a Radiant Heat Energy Source

ASTM E2178

Standard Test Method for Air Permeance of Building Materials Factory Mutual Global Research

FM

FM Approvals

Headquarters Office

1151 Boston-Providence Turnpike

P.O. Box 9102

Norwood, MA 02062

FM 4450

Approval Standard for Class 1 Insulated Steel Deck Roofs

FM 4880

American National Standard for Evaluating Insulated Wall or Wall and Roof/Ceiling Assemblies Plastic Interior Finish Materials Plastic Exterior Building Panels Wall/Ceiling Coating Systems Interior or Exterior Finish Systems

ICC

International Code Council, Inc.

500 New Jersey Ave NW

6th Floor

Washington, DC 20001

IBC

International Building Code®

IMC

International Mechanical Code®

IRC

International Residential Code®

IECC

International Energy Conservation Code®

NFPA

National Fire Protection Association

1 Batterymarch Park

Quincy, MA 02169-7471

NFPA 259

Test Method for Potential Heat of Building Materials

NFPA 268

Standard Test Method for Determining Ignitability of Exterior Wall Assemblies Using a Radiant Heat Energy Source

NFPA 276

Standard Method of Fire Tests for Determining Heat Release Rate of Roofing Assemblies with Combustible Above-Deck Components

NFPA 285

Standard Method of Test for the Evaluation of Flammability Characteristics of Exterior Nonload-Bearing Wall Assemblies Containing Combustible Components Using the Intermediate-Scale, Multistory Test Apparatus

NFPA 286

Standard Method of Fire Test for Evaluating Contribution of Wall and Ceiling Interior Finish to Room Fire Growth

UL

UL LLC

333 Pfingsten Road

Northbrook, IL 60062-2096

UL 263

Standard for Fire Test of Building Construction and Materials

UL 723

Test for Surface Burning Characteristics of Building Materials

UL 790

Tests for Fire Resistance for Roof Covering Materials

UL 1040

Fire Test of Insulated Wall Construction

UL 1256

Fire Tests of Roof Deck Construction

UL 1715

Fire Tests of Interior Finish Material

TABLE 1. PHYSICAL PROPERTIES OF LOW-DENSITY SPRAY-APPLIED FOAM PLASTIC
(nominal core density less than 1.5 pcf)

| PROPERTY | TESTS | VALUE |  | NUMBER OF SPECIMENS | SAMPLE PREPARATION |
| --- | --- | --- | --- | --- | --- |
| Thermal Resistance | ASTM C177, ASTM C518, or ASTM C1363 | Minimum closed cell content of 90% | As reported | 5 at each thickness | (a) 73 ± 2°F (23 ± 1°C) and 50 ± 5% relative humidity for 180 ± 5 days; or (b) 140 ± 2°F (60 ± 1°C) and dry heat for 90 ± 2 days |
|  |  | Closed cell content of less than 90% | As reported | 5 at each thickness | (a) 73 ± 2°F (23 ± 1°C) and 50 ± 5% relative humidity for 30 days min. or (b) 73 ± 2°F (23 ± 1°C) and 50 ± 5% relative humidity for 180 ± 5 days; or (c) 140 ± 2°F (60 ± 1°C) and dry heat for 90 ± 2 days |
| Core Density | ASTM D1622 | As Reported |  | 3 | In accordance with Section 6.3 of the standard |
| Closed cell content | ASTM D6226 | Report value |  | 5 | In accordance with test standard |
| Tensile Strength | ASTM D1623 | 1.0 lbf/in2 (7 kPa) min |  | 5 | In accordance with test standard |
| Dimensional Stabilitya | ASTM D2126 | 15% max total change |  | 2 min | In accordance with aNotes below |

For SI: 1 pfc = 16.02 kg/m3, 1 lbf/in2 = 6.89 kPa

aNotes: Dimensional stability sample preparation for low-density spray-applied foam plastic.

1.	Spray a sufficient quantity of foam to provide at least two specimens measuring a minimum of 4-inch ´ 4-inch (100 mm x 100 mm) ´ thickness determined by the manufacturer (but no less than 1 inch) to a suitable clean and dry substrate. Allow spray-applied foam plastic to cure on the substrate.

2.	Remove spray-applied foam plastic from the substrate and condition the foam to a constant mass but no less than 72 hours at 73.4 ± 4°F (23 ± 2°C) and 50 ± 10% relative humidity prior to cutting the samples.

3.	Cut at least two specimens measuring a minimum of 4-inch ´ 4-inch (100 mm x 100 mm) ´ thickness determined by the manufacturer (minimum 1 inch).

4.	Expose the specimens to 158 ± 4°F (70 ± 2°C) and 97 ± 3% relative humidity for 168 ± 2 hours. Measure the percent change in the length, width and thickness directions of the sample after 24 ± 1 hours and 168 ± 2 hours.

TABLE 2. PHYSICAL PROPERTIES OF MEDIUM-DENSITY SPRAY-APPLIED FOAM PLASTIC
(nominal core density 1.5 – 3.5 pcf)

| PROPERTY |  | TESTS |  |  |  | VALUE/REQUIREMENT | NUMBER OF SPECIMENS |  |  |  | SAMPLE PREPARATION |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Thermal Resistance |  | ASTM C177, ASTM C518, or ASTM C1363 |  |  |  | As reported | 5 at each thickness |  |  |  | Samples shall be conditioned at: (a) 73 ± 2°F (23 ± 1°C) and 50 ± 5% relative humidity for 180 ± 5 days; or (b) 140 ± 2°F (60 ± 1°C) and dry heat for 90 ± 2 days |  |
| Closed cell content | ASTM D6226 |  |  | As reported* |  |  |  |  | 5 |  |  | In accordance with test standard |  |
| Core Density |  | ASTM D1622 |  |  |  | As reported | 3 |  |  |  | In accordance with Section 6.3 of the test standard |  |
| Tensile Strength |  | ASTM D1623 |  |  |  | 15 lbf/in2 (100 kPa) min | 5 |  |  |  | In accordance with test standard |  |
| Compressive Strength |  | ASTM D1621 |  |  |  | 15 lbf/in2 (100 kPa) min | 5 |  |  |  | In accordance with test standard |  |
| Dimensional Stability |  | ASTM D2126 |  |  |  | 15% total change | 2 min |  |  |  | In accordance with ASTM C1029, Section 9.4 and 10.6 or ASTM D2126 |  |

- to be considered closed cell foam Closed Cell Content must be equal or greater than 90%

For SI: 1 pfc = 16.02 kg/m3, 1 lbf/in2 = 6.89 kPaspray

TABLE 3. PHYSICAL PROPERTIES OF MEDIUM-DENSITY  SPRAY-APPLIED FOAM PLASTIC ROOFING FOAM
(nominal core density 2.5 – 3.5 pcf)

| PROPERTY | TESTS | VALUE | NUMBER OF SPECIMENS | SAMPLE PREPARATION |
| --- | --- | --- | --- | --- |
| Core Density | ASTM D1622 | As Reported | 3 | In accordance with test standard |
| Tensile Strength | ASTM D1623 | 40 lbf/in2, minimum | 5 | In accordance with test standard |
| Dimensional Stability | ASTM D2126 | 15% total change max | 2 min | In accordance with test standard |
| Surface Burning Characteristics | IBC-ASTM E84 or UL723 | 75 flame-spread index or less | 3 runs | 2 ft. x 24 ft. |
| Compressive Strength | ASTM D1621 | 40 lbf/in2, minimum | 5 | In accordance with test standard |
| Thermal Resistance at 75°F (24°C) mean temperature | ASTM C177 ASTM C518 ASTM C1363 | As Reported | 5 at each thickness | In accordance with test standard |
| Closed Cell Content | ASTM D6226 | Min 90% | 5 | In accordance with test standard |

TABLE 4. PHYSICAL PROPERTIES OF SPRAY-APPLIED FOAM PLASTIC FOAM FOR SEALING FOAM

| PROPERTY | TESTS | VALUE | NUMBER OF SPECIMENS | SAMPLE PREPARATION |
| --- | --- | --- | --- | --- |
| Core Density | ASTM D1622 | As Reported | 3 | In accordance with test standard |
| Surface Burning Characteristics | IBC-ASTM E84 or UL723 | 75 flame-spread index or less, 450 smoke-developed index or less | 3 runs* | 2 ft. x 24 ft. |
| Adhesion | ASTM D1623 | 5 lbf/in2, minimum | 3 min | In accordance with test standard |

- Sample preparation, dimensions (width(s) of bead (s)) and mounting method to be reported with results.(e.g. ASTM E2690)

FIGURE 1
MEASUREMENT POINTS FOR BURNER SPACING FROM FOAM

(Method A and Method U)

FIGURE 2
TOP VIEW OF WALL CONSTRUCTION

FIGURE 3
SIDE VIEW OF CEILING CONSTRUCTION
(See the table on the following page for requirements related to Figures 2 and 3.)

FIGURE 4

GENERAL ROOM CONSTRUCTION DETAILS (TEST METHOD U)

FIGURE 5

ATTIC HATCH OPENING SIZE AND LOCATION REQUIREMENTS

FIGURE 6

TEST ROOM, SMOKE HOOD AND BURNER CONFIGURATION

FIGURE 7

THERMOCOUPLE LOCATIONS

FIGURE 8

SIDE VIEW OF WALL CONSTRUCTION FOR SILL PLATES AND HEADERS TESTING

| Ignition Source | The standard gas burner shall be used. The burner shall be positioned in the fire test room as indicated in Figure 1. |
| --- | --- |
| Specimen Mounting | The test specimens shall be mounted in accordance with the configuration described in either Configuration A or Configuration B. Whichever configuration is used, the interior room dimensions as required by the NFPA 286 test procedure shall be maintained. |
| Configuration A | When Configuration A is used, the fire test room shall be completely lined with one layer of 5/8-inch-thick (15.9 mm), Type X gypsum wallboard. The spray-applied foam plastic insulation shall be applied directly to the gypsum wallboard at the maximum thickness and density intended for use. The spray-applied foam plastic insulation shall be applied to the three test walls and the test ceiling. If a covering is used over the foam, it shall be applied to both the walls and the ceiling at the same minimum thickness or coverage rate intended for use. |
| Configuration B | When Configuration B is used, the three walls of the test room without the doorway shall be constructed with wood studs sized to the same depth as the test specimen, 93 inches (2362 mm) high, 24 inches (610 mm) on center with a single top and bottom plate, as shown in Figure 2. The exterior side of the walls shall be covered with one layer of 5/8-inch-thick (15.9 mm), Type X gypsum wallboard. The spray-applied foam plastic insulation shall be sprayed to fill each stud cavity and be continuous from the bottom plate to the top plate and from stud to stud. The ceiling of the test room shall be constructed as shown in Figure 3. The ceiling shall consist of wood joists sized to the same depth as the test specimen at 24 inches (610 mm) on center. A total of five joists shall be used and they shall run parallel with the 12-foot length (3.6 m) of the test room (front to back). The two outboard joists shall rest on the top plates of the walls. The exterior side of the ceiling shall be covered with one layer of 5/8-inch-thick (15.9 mm), Type X gypsum wallboard. The spray-applied foam plastic insulation shall be sprayed to fill each joist cavity and will be continuous from the front to the back and from joist to joist. If a coating is used over the foam, it shall be applied to both the walls and the ceiling at the same minimum thickness or coverage rate intended for use. |

Appendix A – Codes and Referenced Standards Correlation Table

| Standard |  | Date of Standard |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Designation | Title | 2006 I-Codes | 2009 I-Codes | 2012 I-Codes | 2015 I-Codes | 2018 I-Codes | 2021 I-Codes | 2024 I-Codes |
| AATCC 127 | Test Method for Water Resistance: Hydrostatic Pressure Test | Not referenced in IBC, IRC, IECC |  |  |  |  |  |  |
| ASTM C177 | Test Method for Steady-State Heat Flux Measurements and Thermal Transmission Properties by Means of the Guarded Hot Plate Apparatus | Not referenced in IBC, IRC, IECC |  |  |  |  |  |  |
| ASTM C208 | Standard Specification for Cellulosic Fiber Insulating Board | 1995 (2001) | 1995 (2001) | 2008a | 2012 | 2012 | 2012 (2017)E1 | 2022 |
| ASTM C518 | Test Method for Steady-State Heat Flux Measurements and Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus | Not referenced in IBC, IRC, IFC, IECC |  |  |  |  |  |  |
| ASTM C840 | Standard Specification for Application and Finishing of Gypsum Board | 2004 | 2007 | 2008 | 2011 | 2013 | 2018a | 2020 |
| ASTM C1029 | Specification for Spray-Applied Rigid Cellular Polyurethane Thermal Insulation | 2002 | 2005a | 2008 | 2013 | 2015 | 2015 | 2020 |
| ASTM C1363 | Standard Test Method for Thermal Performance of Building Materials and Envelope Assemblies by Means of a Hot Box Apparatus | "2005 (IECC only)" | "2005 (IECC only)" | "2005 (IECC only)" | "2011 (IECC only)" | "2011 (IECC only)" | "2011 (IECC only)" | "2019 (IECC only)" |
| ASTM D1621 | Test Method for Compressive Properties of Rigid Cellular Plastics | Not referenced in IBC, IRC, IECC |  |  |  |  |  |  |
| ASTM D1622 | Test Method for Determining Apparent Density of Rigid Cellular Plastics | Not referenced in IBC, IRC, IECC |  |  |  |  |  |  |
| ASTM D1623 | Test Method for Tensile and Tensile Adhesion Properties of Rigid Cellular Plastics (Type B Specimen) | Not referenced in IBC, IRC, IECC |  |  |  |  |  |  |
| ASTM D2126 | Test Method for Response of Rigid Cellular Plastics to Thermal and Humid Aging | Not referenced in IBC, IRC, IECC |  |  |  |  |  |  |
| ASTM D2856 | Standard Test Method for Open-Cell Content of Rigid Cellular Plastics by the Air Pycnometer | Not referenced in IBC, IRC, IECC |  |  |  |  |  |  |
| ASTM D6226 | Standard Test Method for Open-Cell Content of Rigid Cellular Plastics | Not referenced in IBC, IRC, IECC |  |  |  |  |  |  |
| ASTM D7425 | Standard Specification for Spray Polyurethane Foam Used for Roofing Applications | -- | -- | -- | "2011 (IRC only) | 2013 | 2013 | 2013 (2019) |
| ASTM E72 | Standard Test Methods of Conductiong Strenth Tests of Panels for Building Construction | Not referenced in IBC, IRC, IFC, IECC |  |  |  |  |  |  |
| ASTM E84 | Test Methods for Surface Burning Characteristics of Building Materials | 2004 | 2007 | 2009 | 2013a | 2016 | 2018b | 2021a |
| ASTM E96/E96M | Test Method for Water Vapor Transmission of Materials | 2000E1 | 2005 | 2005 | 2013 | 2015 | 2016 | 2021 |
| ASTM E108 | Test Method for Fire Tests of Roof Coverings | 2004 | 2007a | 2007 | 2011 | 2016 | 2017 | 2020a |
| ASTM E119 | Test Methods for Fire Tests of Building Construction and Materials | 2000 | 2007 | 2008a | 2012a | 2016 | 2018b | 2020 |
| ASTM E283/E283M | Test Method for Determining the Rate of Air Leakage through Exterior Windows Curtain Walls and Doors under Specified Pressure Differences across the Specimen | 2004 | 2004 | 2004 | 2004 | 2004 (2012) | 2004 (2012) | 2019 |
| ASTM E331 | Standard Test Method for Water Penetration of Exterior Windows, Skylights, Doors and Curtain Walls by Uniform Static Air Pressure Difference | 2000 | 2000 | 2000 (2009) | 2000 (2009) | 2000 (2009) | 2000 (2016) | 2000 (2016) |
| ASTM E970 | Test Method for Critical Radiant Flux of Exposed Attic Floor Insulation Using a Radiant Heat Energy Source | 2000 | 2000 | 2008a | 2010 | 2014 | 2017 | 2017 |
| ASTM E2178 | Standard Test Method for Air Permeance of Building Materials Factory Mutual Global Research | - | 2003 | 2003 | 2013 | 2013 | 2013 | 2021a |
| FM 4450 | Approval Standard for Class 1 Insulated Steel Deck Roofs | 1989 with Supplements through July 1992 | "1989 with Supplements through July 1992 (IRC only)" | "1989 with Supplements through July 1992 (IRC only)" | "1989 with Supplements through July 1992 (IRC only)" | 1989 with Supplements through July 1992 | 1989 with Supplements through July 1992 | 1989 with Supplements through July 1992 |
| FM 4880 | American National Standard for Evaluating Insulated Wall or Wall and Roof/Ceiling Assemblies Plastic Interior Finish Materials Plastic Exterior Building Panels Wall/Ceiling Coating Systems Interior or Exterior Finish Systems | 2001 | 2005 | 2005 | 2010 | 2015 | 2017 | 2017 |
| NFPA 259 | Test Method for Potential Heat of Building Materials | 2003 | 2003 | 2008 | 2013 | 2018 | 2018 | 2023 |
| NFPA 268 | Standard Test Method for Determining Ignitability of Exterior Wall Assemblies Using a Radiant Heat Energy Source | 2001 | 2007 | 2012 | 2012 | 2017 | 2017 | 2022 |
| NFPA 275 | Standard Method of Fire Tests for the Evaluation of Thermal Barriers Used over Foam Plastic Insulation | -- | -- | 2015 | 1013 | 2017 | 2017 | 2022 |
| NFPA 276 | Standard Method of Fire Tests for Determining Heat Release Rate of Roofing Assemblies with Combustible Above-Deck Components | -- | -- | -- | "2011 (IBC only) | 2015 | 2019 | 2023 |
| NFPA 285 | Standard Method of Test for the Evaluation of Flammability Characteristics of Exterior Nonload-Bearing Wall Assemblies Containing Combustible Components Using the Intermediate-Scale, Multistory Test Apparatus | 1998 | 2006 | 2011 | 2012 | 2012 | 2019 | 2023 |
| NFPA 286 | Standard Method of Fire Test for Evaluating Contribution of Wall and Ceiling Interior Finish to Room Fire Growth | 2000 | 2006 | 2011 | 2015 | 2015 | 2019 | 2024 |
| 29 CFR, Part 1926, Subpart J, Standard 1926.352 | Safety and Health Regulations for Construction | Not referenced in IBC, IRC, IECC |  |  |  |  |  |  |
| UL 263 | Standard for Fire Test of Building Construction and Materials | -- | 2003 | 2003 with Revisions through October 2007 | 2011 | 2011 with Revisions through June 2015 | 2011 with Revisions through March 2018 | 2011 with Revisions through August 2021 |
| UL 723 | Test for Surface Burning Characteristics of Building Materials | -- | 2003 with Revisions through May 2005 | 2008 | 2008 with Revisions through September 2010 | 2008 with Revisions through August 2013 | 2018 | 2018 |
| UL 790 | Tests for Fire Resistance for Roof Covering Materials | 1998 with Revisions through July 1998 | 2004 | 2004 with Revisions through October 2008 | 2004 with Revisions through October 2008 | 2004 with Revisions through July 2014 | 2004 with Revisions through October 2018 | 2004 with Revisions through October 2018 |
| UL 1040 | Fire Test of Insulated Wall Construction | 1996 with Revisions through April 2001 (IBC) and June 2021 (IRC) | 1996 with Revisions through April 2001 (IBC) and June 2021 (IRC) | 1996 | 1996 with Revisions through October 2012 | 1996 with Revisions through October 2012 | 1996 with Revisions through April 2017 | 1996 with Revisions through April 2017 |
| UL 1256 | Fire Tests of Roof Deck Construction | 2002 | 2002 | 2002 | 2002 with Revisions through January 2007 | 2002 with Revisions through July 2013 | 2002 with Revisions through August 2018 | 2002 with Revisions through August 2018 |
| UL 1715 | Fire Tests of Interior Finish Material | 1997 with Revisions through October 2002 (IBC) and March 2004 (IRC) | 1997 with Revisions through March 2004 | 1997 with Revisions through March 2004 | 1997 with Revisions through October 2002 (IBC) and March 2004 (IRC) | 1997 with Revisions through January 2013 | 1997 with Revisions through January 2013 | 1997 with Revisions through April 2017 |

Appendix B – XXXXX